## Plot Data (hidden)
Psychrometric Chart Plots
| p | #REF! | kPa
|  | Relative Humidity Lines | [9 empty] | Enthalpy Lines
Values in table are W (kg/kg))
|  | RH = | [9 empty] | H | Dry-bulb |  | H
| Dry-bulb [C] | 10% | 20% | 30% | 40% | 50% | 60% | 70% | 80% | 90% | 100% | [kJ/kg] | [C] | w | [kJ/kg] | RH
| 0 | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | 10 | 0 | #NAME? | #NAME? | 105.9% | <--- This line handled a little differently…
| 3 | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | 10 | 9.9404 | #NAME? | #NAME?
| 6 | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | 20 | 5.7081 | #NAME? | #NAME?
| 9 | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | 20 | 19.8807 | #NAME? | #NAME?
| 12 | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | 30 | 10.3073 | #NAME? | #NAME?
| 15 | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | 30 | 29.8211 | #NAME? | #NAME?
| 18 | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | 40 | 14.2694 | #NAME? | #NAME?
| 21 | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | 40 | 39.7614 | #NAME? | #NAME?
| 24 | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | 50 | 17.7179 | #NAME? | #NAME?
| 27 | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | 50 | 49.7018 | #NAME? | #NAME?
| 30 | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | 60 | 20.7523 | #NAME? | #NAME?
| 33 | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | 60 | 59.6421 | #NAME? | #NAME?
| 36 | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | 70 | 23.45 | #NAME? | #NAME?
| 39 | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | 70 | 69.5825 | #NAME? | #NAME?
| 42 | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | 80 | 25.871 | #NAME? | #NAME?
| 45 | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | 80 | 79.5229 | #NAME? | #NAME?
| 48 | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | 90 | 28.0619 | #NAME? | #NAME?
| 51 | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | 90 | 89.4632 | #NAME? | #NAME?
| 54 | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | 100 | 30.0592 | #NAME? | #NAME?
[12 empty] | 100 | 99.4036 | #NAME? | #NAME?
[12 empty] | 110 | 31.8918 | #NAME? | #NAME?
[12 empty] | 110 | 109.3439 | #NAME? | #NAME?
[12 empty] | 120 | 33.583 | #NAME? | #NAME?
[12 empty] | 120 | 119.2843 | #NAME? | #NAME?
This sheet is used to plot the lines on the psychrometric chart. The relative humidity lines update automatically whenever the atmospheric pressure is changed. The constant enthalpy lines are recalculated using a macro whenever the data is updated on Sheet1.
DON'T DELETE THIS SHEET!
(it provides source data for the chart)

## Forced Evaporation
Model of Forced Evaporation from a Water Surface, with user choice of wind function | [6 empty] | Wind Functions of the form f(W) = a + bW + cW2 | [8 empty] | a | b | c | maximum W (m/s) | [12 empty] | Initial Guess at Solution based on quadratic fits to ratio of temperature increase to heat loading | [67 empty] | Constants used in formulae |  |  | SOURCE for constant | [10 empty] | Block for optimization of initial guess at final T | [6 empty] | Results ------------------------------------------------------------------------------------------------------------------------------------------------------------
[7 empty] | These formulas use windspeed in m/s and give f(W) in mm/(day*kPa) following the format of McJannet and others (2012). |  |  |  | cooling lake |  | Harbeck, 1964 |  |  | 0 | 1.4617 | 0 | - - |  | Calculations for un-heated condition ---------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------- | [10 empty] | These averaged coefficients produce good convergence for all wind functions - see columns DZ through EN | [67 empty] | constant | 252.1644 | calorie per Btu | http://www.nist.gov/pml/wmd/metric/upload/SP1038.pdf |  |  |  |  | Constants |  |  | SOURCE for constants | [5 empty] | Solver changes these |  | …to minimize this |  | Harbeck | Ward | Brady | Anderson | Fulford | Gulliver | Webster | average over 7 wind functions
[11 empty] | cooling lake |  | Ward, 1980 |  |  | 0 | 1.3529 | 0 | - - | rHf | [11 empty] | 4119.6015 | constant |  |  | T1 | [63 empty] | constant | 3785.412 | cc/gal | ditto |  |  |  |  | ϵr | 0.97 | per day | Ward 1980 |  | water emissivity |  |  |  | constant | 3181.3458 | RMSE |  | 5279.4253 | 5440.3446 | 3061.3315 | 6218.6188 | 2395.6393 | 2565.0086 | 3876.8427 | 4119.6015
FEWS Version 3.104 - 2013/9/24 - Timothy H. Diehl | [10 empty] | cooling ponds |  | Brady and others, 1969 |  |  | 2.466 | 0 | 0.1234 | - - |  | saturation vapor pressure calculated on the basis of wet bulb temperature | air vapor pressure | [6 empty] | water density | heat of vapor-ization | saturation vapor pressure at water temperature | -48.7754 | x T | [66 empty] | constant | 453.5924 | grams per pound | ditto |  |  |  |  | σ | 1.171e-07 | cal/cm2/K4/day | Ward 1980 |  | the Stefan-Boltzman constant |  |  |  | x T | -38.9332 | 299.5147 |  | -49.8736 | -51.2838 | -48.8104 | -58.1181 | -40.6347 | -43.6364 | -49.0706 | -48.7754
[7 empty] | Input wind function coefficients |  |  |  | big lake |  | Anderson, 1954 |  |  | 0 | 0.92 | 0 | 8.25 | [12 empty] | -339.157 | x W | [8 empty] | Second iteration | [6 empty] | Third iteration | [6 empty] | Fourth iteration | [6 empty] | Fifth iteration | [6 empty] | Sixth iteration | [6 empty] | Seventh iteration | [6 empty] | Eighth iteration | [6 empty] | Ninth iteration | [8 empty] | constant | 4.184 | Joules per calorie | ditto |  |  |  |  | cp | 0.24 | cal/ g/ K | Ward 1980 |  | specific heat of air at a constant pressure |  |  |  | x W | -162.1953 |  |  | -593.704 | -599.7274 | -78.5589 | -612.9317 | -100.0964 | -93.8343 | -295.2461 | -339.157
|  | Input values in purple |  |  |  |  | a | b | c |  | river channel |  | Fulford and Sturm, 1984 |  |  | 3.2 | 0.8 | 0 | 3.75 | [12 empty] | -359.7976 | x MW/a | [7 empty] | rH1 | T2 | [5 empty] | rH2 | T3 | [50 empty] | constant | 1055.056 | Joules per Btu | ditto |  |  |  |  | ϵ | 0.622 |  | Ward 1980 |  | the molecular weight ratio of water vapor to dry air |  |  |  | x MW/a | -358.4268 |  |  | -434.8922 | -463.9111 | -291.8205 | -625.7714 | -170.4859 | -203.7668 | -327.935 | -359.7976
| z | 596 | feet | elevation |  |  | 2.47 | 0 | 0.12 |  | stream |  | Gulliver and Stefan, 1986 |  |  | 2.96 | 0.64 | 0 | 5.75 | [12 empty] | 0.25368 | x T2 | [8 empty] | curve is nearly linear, so converge without any weight on previous guess | [57 empty] | constant | 252.1644 | Calories per Btu | calculated | [5 empty] | also see Ward equation 1 2 3 14 tab | [7 empty] | x T2 | -0.0097725 |  |  | 0.24376 | 0.24582 | 0.26709 | 0.25582 | 0.24621 | 0.25665 | 0.2604 | 0.25368
| z | 181.6608 | meters | elevation |  |  | Enter purple coefficients manually |  |  |  | lake |  | Webster and Sherman, 1995 |  |  | 1.04 | 1.05 | 0 | 5 | [12 empty] | 12.5619 | x W2 | [8 empty] | Values of these variables have to be recalculated at each estimated heated temperature | [74 empty] | x W2 | 2.3092 |  |  | 24.338 | 24.4319 | -0.61008 | 24.0993 | 2.7382 | 2.4075 | 10.5284 | 12.5619
Constants and references in columns DO - DY | [6 empty] | Summary output section - heat loss rates are in cal/(cm2sec) | [8 empty] | Maximum | Annual results for 12-month data | [14 empty] | 46.1229 | x (MW/a) 2 | Maximum | [58 empty] | Output values for evaporation depth |  |  | Output | [11 empty] | p | 991.6166 | mbar | [6 empty] | x (MW/a) 2 | 46.1252 |  |  | 59.411 | 63.8008 | 33.4971 | 89.0248 | 16.3432 | 20.596 | 40.1876 | 46.1229
| Input environmental data and heat loading | [5 empty] | Final values - Solution with added heat |  |  |  | Increment from initial to final conditions |  |  |  | increment % | 2.254e-14% | 180.0905 | 286.8108 | 73.7867 |  |  |  |  | wind function coefficients |  |  | 1.1574e-07 | conversion factor | Initial |  |  | These values averaged from fits to 7 wind functions |  | 2.254e-14% |  |  |  | Increment in heat loss by mode | [6 empty] | Increment in heat loss by mode | [6 empty] | Increment in heat loss by mode | [6 empty] | Increment in heat loss by mode | [6 empty] | Increment in heat loss by mode | [6 empty] | Increment in heat loss by mode | [6 empty] | Increment in heat loss by mode | [6 empty] | Increment in heat loss by mode |  |  |  | Output |  |  |  |  | Increment in heat loss by mode |  |  |  | This section converts evaporation to gallons per million Btu of condenser duty for comparison to literature values | [7 empty] | pressure function cite on "altitude vs. air pressure" page | [5 empty] | This section is left to show how the coefficients for the intitial guess were calculated - the data set used for optimization contained a wide range of temperature, windspeed, and heat loading.
| Days per month | Dry bulb air temp- erature Ta (oC) | Wet bulb air temp- erature Twb (oC) | Natural water temp- erature T (oC) | Wind speed at 2m W (mph) | Added heat load rH (MW/ acre) | Heated water temperature T' (oC) | Asterisk indicates declining precision at T' > 50 | Evaporated gallons per million Btu of condenser duty | Evaporated gallons per MWh thermal condenser duty | Heating of water (oC) | Added evapo-ration (cm/ month) | Evapo- rative heat loss incre- ment | Total heat loss incre- ment | Evaporative cooling as percent of added heat | Percent change in T' in last iteration | Annual mean forced evaporation (gal/ MWht condenser duty) | Annual mean forced evaporation (gal/Mwe) | Added evapo- ration (cm) | input heat load, cal/(cm2 sec) | e(Twb) in mbar | ea in mbar | windspeed in m/s | a | b | c | f(W) in mm/ (day*kPa) | f(W) in cm/(sec*mbar) | ρ (g/cm3) | L (cal/g) | e(T) (mbar) | initial estimated ratio of delta T to heat loading | final ratio of delta T to heat loading | Percent change in T' in last iteration | Final heated water temperature T' (oC) | Initial guess at T' | e(T') | rE | rC | rR | Increment in total heat loss rH | Estimated heated water temperature T' (oC) | Percent change in T' from previous iteration | e(T') | rE | rC | rR | Increment in total heat loss rH | Estimated heated water temperature T' (oC) | Percent change in T' from previous iteration | e(T') | rE | rC | rR | Increment in total heat loss rH | Estimated heated water temperature T' (oC) | Percent change in T' from previous iteration | e(T') | rE | rC | rR | Increment in total heat loss rH | Estimated heated water temperature T' (oC) | Percent change in T' from previous iteration | e(T') | rE | rC | rR | Increment in total heat loss rH | Estimated heated water temperature T' (oC) | Percent change in T' from previous iteration | e(T') | rE | rC | rR | Increment in total heat loss rH | Estimated heated water temperature T' (oC) | Percent change in T' from previous iteration | e(T') | rE | rC | rR | Increment in total heat loss rH | Estimated heated water temperature T' (oC) | Percent change in T' from previous iteration | e(T') | rE | rC | rR | Increment in total heat loss rH | Estimated heated water temperature T' (oC) | Percent change in T' from previous iteration | ρ (g/cm3) | L (cal/g) | e(T') | rE | rC | rR | Increment in total heat loss rH | Heat of vaporization (cal/cc) | Volumetric heat of vaporization (Btu/gal) | Percent forced evaporation | Condenser duty per evaporated volume (MMBtu/gal) | Evaporated volume per condenser duty (gal/MMBtu) | Evaporated volume per condenser duty (gal/MWh thermal) | density at heated temperature (pounds per gallon) | Heat of vaporization (Btu/lb) | [6 empty] | Natural water temp- erature T (oC) | Wind speed at 2m W (mph) | Added heat load rH (MW/ acre) | final ratio | predicted ratio | squared error | absolute error
Jan | 31 | -5.4229 | -6.7858 | 0.15087 | 11.1197 | 0.5 | 5.5091 |  | 40.5525 | 138.3653 | 5.3583 | 4.8149 | 0.001071 | 0.002953 | 36.27% | 0% |  | Plant characteristics |  | 0.002953 | 3.6786 | 2.7936 | 4.9712 | 2.47 | 0 | 0.12 | 5.4356 | 6.2912e-07 | 0.99984 | 595.8178 | 6.1751 | 1725.8068 | 1814.5318 | 0% | 5.5091 | 5.2471 | 8.8698 | 0.0010099 | 0.0012265 | 0.00056257 | 0.002799 | 5.5274 | 5.341% | 9.0443 | 0.0010753 | 0.001294 | 0.00059442 | 0.0029638 | 5.5091 | -0.3317% | 9.0328 | 0.001071 | 0.0012896 | 0.00059234 | 0.0029529 | 5.5091 | 0.001153% | 9.0329 | 0.001071 | 0.0012896 | 0.00059234 | 0.002953 | 5.5091 | 2.798e-07% | 9.0329 | 0.001071 | 0.0012896 | 0.00059234 | 0.002953 | 5.5091 | -2.257e-13% | 9.0329 | 0.001071 | 0.0012896 | 0.00059234 | 0.002953 | 5.5091 | 0% | 9.0329 | 0.001071 | 0.0012896 | 0.00059234 | 0.002953 | 5.5091 | 0% | 9.0329 | 0.001071 | 0.0012896 | 0.00059234 | 0.002953 | 5.5091 | 0% | 0.99983 | 595.8997 | 9.0329 | 0.001071 | 0.0012896 | 0.00059234 | 0.002953 | 595.7984 | 8943.9365 | 36.27% | 0.024659 | 40.5525 | 138.3653 | 8.344 | 1071.9021 | 86400 | seconds per day |  |  |  |  | 0.15087 | 11.1197 | 0.5 | 1814.5318 | 1489.754 | 105480.6485 | 324.7778
Feb | 28 | -4.6088 | -6.3573 | 0.18946 | 10.4617 | 0.5 | 5.8061 |  | 40.2806 | 137.4374 | 5.6166 | 4.3197 | 0.0010639 | 0.002953 | 36.03% | 0% |  | 16% |  | 0.002953 | 3.8015 | 2.6656 | 4.6771 | 2.47 | 0 | 0.12 | 5.095 | 5.897e-07 | 0.99984 | 595.7967 | 6.1924 | 1768.7089 | 1902.0273 | 0% | 5.8061 | 5.4124 | 8.9724 | 0.00097656 | 0.0011783 | 0.0005772 | 0.002732 | 5.8348 | 7.804% | 9.2392 | 0.0010703 | 0.0012736 | 0.00062532 | 0.0029692 | 5.806 | -0.4949% | 9.2208 | 0.0010638 | 0.001267 | 0.00062203 | 0.0029529 | 5.8061 | 0.00258% | 9.2209 | 0.0010639 | 0.0012671 | 0.00062204 | 0.002953 | 5.8061 | 9.838e-07% | 9.2209 | 0.0010639 | 0.0012671 | 0.00062204 | 0.002953 | 5.8061 | -2.05e-12% | 9.2209 | 0.0010639 | 0.0012671 | 0.00062204 | 0.002953 | 5.8061 | -6.119e-14% | 9.2209 | 0.0010639 | 0.0012671 | 0.00062204 | 0.002953 | 5.8061 | 4.589e-14% | 9.2209 | 0.0010639 | 0.0012671 | 0.00062204 | 0.002953 | 5.8061 | 0% | 0.99983 | 595.8997 | 9.2209 | 0.0010639 | 0.0012671 | 0.00062204 | 0.002953 | 595.7984 | 8943.9362 | 36.03% | 0.024826 | 40.2806 | 137.4374 | 8.344 | 1071.9021 | [6 empty] | 0.18946 | 10.4617 | 0.5 | 1902.0273 | 1562.1867 | 115491.6469 | 339.8406
Mar | 31 | 0.83813 | -1.5688 | 2.7142 | 10.7886 | 0.5 | 7.8814 |  | 44.0119 | 150.1685 | 5.1672 | 5.2256 | 0.0011624 | 0.002953 | 39.36% | 2.254e-14% |  | Non-condenser heat loss as percent of fuel heat |  | 0.002953 | 5.446 | 3.8735 | 4.8232 | 2.47 | 0 | 0.12 | 5.2616 | 6.0898e-07 | 0.99992 | 594.4207 | 7.4227 | 1623.8163 | 1749.8247 | 2.254e-14% | 7.8814 | 7.5093 | 10.3675 | 0.0010659 | 0.0011172 | 0.00054333 | 0.0027264 | 7.9078 | 5.306% | 10.6532 | 0.0011693 | 0.00121 | 0.00058975 | 0.0029691 | 7.8813 | -0.3349% | 10.634 | 0.0011624 | 0.0012039 | 0.00058666 | 0.0029529 | 7.8814 | 0.001728% | 10.6341 | 0.0011624 | 0.0012039 | 0.00058668 | 0.002953 | 7.8814 | 6.333e-07% | 10.6341 | 0.0011624 | 0.0012039 | 0.00058668 | 0.002953 | 7.8814 | -1.138e-12% | 10.6341 | 0.0011624 | 0.0012039 | 0.00058668 | 0.002953 | 7.8814 | -1.352e-13% | 10.6341 | 0.0011624 | 0.0012039 | 0.00058668 | 0.002953 | 7.8814 | 7.888e-14% | 10.6341 | 0.0011624 | 0.0012039 | 0.00058668 | 0.002953 | 7.8814 | -2.254e-14% | 0.99983 | 595.8997 | 10.6341 | 0.0011624 | 0.0012039 | 0.00058668 | 0.002953 | 595.7984 | 8943.9365 | 39.36% | 0.022721 | 44.0119 | 150.1685 | 8.344 | 1071.9021 | Constants used in formulae |  |  |  | SOURCE for constant |  | 2.7142 | 10.7886 | 0.5 | 1749.8247 | 1426.8393 | 104319.6176 | 322.9855
Apr | 30 | 7.3674 | 3.6463 | 8.7246 | 10.7637 | 0.5 | 13.1604 |  | 52.5266 | 179.2207 | 4.4358 | 6.0354 | 0.0013873 | 0.002953 | 46.98% | 0% |  |  |  | 0.002953 | 7.9288 | 5.4833 | 4.8121 | 2.47 | 0 | 0.12 | 5.2487 | 6.0749e-07 | 0.99979 | 591.1451 | 11.2608 | 1349.8015 | 1502.127 | 0% | 13.1604 | 12.7106 | 14.6859 | 0.0012297 | 0.00092629 | 0.00047948 | 0.0026355 | 13.1907 | 3.778% | 15.1548 | 0.0013981 | 0.0010379 | 0.00053862 | 0.0029746 | 13.1602 | -0.2317% | 15.1245 | 0.0013872 | 0.0010308 | 0.00053484 | 0.0029528 | 13.1604 | 0.001582% | 15.1247 | 0.0013873 | 0.0010308 | 0.00053487 | 0.002953 | 13.1604 | 7.327e-07% | 15.1247 | 0.0013873 | 0.0010308 | 0.00053487 | 0.002953 | 13.1604 | -2.335e-12% | 15.1247 | 0.0013873 | 0.0010308 | 0.00053487 | 0.002953 | 13.1604 | -1.35e-14% | 15.1247 | 0.0013873 | 0.0010308 | 0.00053487 | 0.002953 | 13.1604 | 0% | 15.1247 | 0.0013873 | 0.0010308 | 0.00053487 | 0.002953 | 13.1604 | 0% | 0.99983 | 595.8997 | 15.1247 | 0.0013873 | 0.0010308 | 0.00053487 | 0.002953 | 595.7984 | 8943.9369 | 46.98% | 0.019038 | 52.5266 | 179.2207 | 8.344 | 1071.9021 | 252.1644 |  | calorie per Btu |  | http://www.nist.gov/pml/wmd/metric/upload/SP1038.pdf |  | 8.7246 | 10.7637 | 0.5 | 1502.127 | 1194.9613 | 94350.7671 | 307.1657
May | 31 | 13.7817 | 9.5444 | 13.0203 | 9.6388 | 0.5 | 17.3051 |  | 57.6262 | 196.6207 | 4.2847 | 6.842 | 0.001522 | 0.002953 | 51.54% | 0% |  |  |  | 0.002953 | 11.9011 | 9.0975 | 4.3092 | 2.47 | 0 | 0.12 | 4.6983 | 5.4378e-07 | 0.99942 | 588.8039 | 14.9869 | 1257.183 | 1450.9897 | 0% | 17.3051 | 16.7328 | 19.0396 | 0.0012969 | 0.00077197 | 0.0004665 | 0.0025353 | 17.3443 | 3.655% | 19.7922 | 0.0015377 | 0.00089913 | 0.00054509 | 0.0029819 | 17.3047 | -0.2284% | 19.7427 | 0.0015218 | 0.0008909 | 0.00053998 | 0.0029527 | 17.3051 | 0.002071% | 19.7431 | 0.001522 | 0.00089097 | 0.00054003 | 0.002953 | 17.3051 | 1.297e-06% | 19.7431 | 0.001522 | 0.00089097 | 0.00054003 | 0.002953 | 17.3051 | -7.37e-12% | 19.7431 | 0.001522 | 0.00089097 | 0.00054003 | 0.002953 | 17.3051 | -2.053e-14% | 19.7431 | 0.001522 | 0.00089097 | 0.00054003 | 0.002953 | 17.3051 | 0% | 19.7431 | 0.001522 | 0.00089097 | 0.00054003 | 0.002953 | 17.3051 | 0% | 0.99983 | 595.8997 | 19.7431 | 0.001522 | 0.00089097 | 0.00054003 | 0.002953 | 595.7984 | 8943.9369 | 51.54% | 0.017353 | 57.6262 | 196.6207 | 8.344 | 1071.9021 | 3785.412 |  | cc/gal |  | ditto |  | 13.0203 | 9.6388 | 0.5 | 1450.9897 | 1156.255 | 86868.5369 | 294.7347
Jun | 30 | 18.7995 | 11.6314 | 17.2538 | 8.5698 | 0.5 | 21.3586 |  | 62.2742 | 212.4796 | 4.1047 | 7.1554 | 0.0016447 | 0.002953 | 55.7% | 0% |  |  |  | 0.002953 | 13.6784 | 8.9244 | 3.8313 | 2.47 | 0 | 0.12 | 4.2314 | 4.8975e-07 | 0.99883 | 586.4967 | 19.6792 | 1201.2455 | 1390.0327 | 0% | 21.3586 | 20.8011 | 24.5565 | 0.0013993 | 0.00066393 | 0.00046529 | 0.0025285 | 21.3966 | 2.863% | 25.4713 | 0.0016618 | 0.00077539 | 0.00054507 | 0.0029822 | 21.3582 | -0.1793% | 25.4115 | 0.0016446 | 0.00076821 | 0.00053992 | 0.0029527 | 21.3586 | 0.001636% | 25.412 | 0.0016447 | 0.00076828 | 0.00053996 | 0.002953 | 21.3586 | 1.025e-06% | 25.412 | 0.0016447 | 0.00076828 | 0.00053996 | 0.002953 | 21.3586 | -5.905e-12% | 25.412 | 0.0016447 | 0.00076828 | 0.00053996 | 0.002953 | 21.3586 | -1.663e-14% | 25.412 | 0.0016447 | 0.00076828 | 0.00053996 | 0.002953 | 21.3586 | 0% | 25.412 | 0.0016447 | 0.00076828 | 0.00053996 | 0.002953 | 21.3586 | 0% | 0.99983 | 595.8997 | 25.412 | 0.0016447 | 0.00076828 | 0.00053996 | 0.002953 | 595.7984 | 8943.9369 | 55.7% | 0.016058 | 62.2742 | 212.4796 | 8.344 | 1071.9021 | 453.5924 |  | grams per pound |  | ditto |  | 17.2538 | 8.5698 | 0.5 | 1390.0327 | 1118.6153 | 73667.405 | 271.4174
Jul | 31 | 21.5969 | 15.0379 | 21.9432 | 7.8849 | 0.5 | 25.6926 |  | 67.4047 | 229.9848 | 3.7494 | 8.003 | 0.0017802 | 0.002953 | 60.29% | 0% |  | 32.4% |  | 0.002953 | 17.0835 | 12.7166 | 3.5251 | 2.47 | 0 | 0.12 | 3.9611 | 4.5847e-07 | 0.99792 | 583.941 | 26.3371 | 1109.8687 | 1269.7038 | 0% | 25.6926 | 25.2206 | 32.0882 | 0.0015365 | 0.00057372 | 0.00045031 | 0.0025605 | 25.723 | 1.992% | 33.0602 | 0.0017961 | 0.00066166 | 0.00052066 | 0.0029785 | 25.6923 | -0.119% | 33.0002 | 0.0017801 | 0.0006563 | 0.00051636 | 0.0029528 | 25.6926 | 0.0009473% | 33.0007 | 0.0017802 | 0.00065634 | 0.0005164 | 0.002953 | 25.6926 | 4.883e-07% | 33.0007 | 0.0017802 | 0.00065634 | 0.0005164 | 0.002953 | 25.6926 | -2.005e-12% | 33.0007 | 0.0017802 | 0.00065634 | 0.0005164 | 0.002953 | 25.6926 | 0% | 33.0007 | 0.0017802 | 0.00065634 | 0.0005164 | 0.002953 | 25.6926 | 0% | 33.0007 | 0.0017802 | 0.00065634 | 0.0005164 | 0.002953 | 25.6926 | 0% | 0.99983 | 595.8997 | 33.0007 | 0.0017802 | 0.00065634 | 0.0005164 | 0.002953 | 595.7984 | 8943.9371 | 60.29% | 0.014836 | 67.4047 | 229.9848 | 8.344 | 1071.9022 | 4.184 |  | Joules per calorie |  | ditto |  | 21.9432 | 7.8849 | 0.5 | 1269.7038 | 1019.3122 | 62695.96 | 250.3916
Aug | 31 | 20.9228 | 15.4172 | 19.8151 | 7.4649 | 0.5 | 23.9383 |  | 64.4527 | 219.9126 | 4.1231 | 7.6526 | 0.0017023 | 0.002953 | 57.65% | 0% |  | Net thermal efficiency |  | 0.002953 | 17.5053 | 13.8381 | 3.3373 | 2.47 | 0 | 0.12 | 3.8065 | 4.4057e-07 | 0.99837 | 585.1008 | 23.1049 | 1252.5903 | 1396.2587 | 0% | 23.9383 | 23.514 | 28.97 | 0.0015094 | 0.0006225 | 0.00049843 | 0.0026304 | 23.9677 | 1.929% | 29.772 | 0.0017158 | 0.00069885 | 0.00056087 | 0.0029755 | 23.9381 | -0.1237% | 29.719 | 0.0017022 | 0.00069386 | 0.00055678 | 0.0029528 | 23.9383 | 0.000869% | 29.7194 | 0.0017023 | 0.00069389 | 0.00055681 | 0.002953 | 23.9383 | 4.26e-07% | 29.7194 | 0.0017023 | 0.00069389 | 0.00055681 | 0.002953 | 23.9383 | -1.514e-12% | 29.7194 | 0.0017023 | 0.00069389 | 0.00055681 | 0.002953 | 23.9383 | 2.968e-14% | 29.7194 | 0.0017023 | 0.00069389 | 0.00055681 | 0.002953 | 23.9383 | 0% | 29.7194 | 0.0017023 | 0.00069389 | 0.00055681 | 0.002953 | 23.9383 | 0% | 0.99983 | 595.8997 | 29.7194 | 0.0017023 | 0.00069389 | 0.00055681 | 0.002953 | 595.7984 | 8943.9367 | 57.65% | 0.015515 | 64.4527 | 219.9126 | 8.344 | 1071.9021 | 1055.056 |  | Joules per Btu |  | ditto |  | 19.8151 | 7.4649 | 0.5 | 1396.2587 | 1156.2737 | 57592.7975 | 239.985
Sep | 30 | 16.2351 | 10.9189 | 16.7567 | 8.3158 | 0.5 | 21.0007 |  | 61.4141 | 209.5451 | 4.2441 | 7.0566 | 0.001622 | 0.002953 | 54.93% | 0% |  |  |  | 0.002953 | 13.047 | 9.524 | 3.7177 | 2.47 | 0 | 0.12 | 4.1286 | 4.7784e-07 | 0.99891 | 586.7676 | 19.0686 | 1253.4778 | 1437.2173 | 0% | 21.0007 | 20.4582 | 24.0428 | 0.0013932 | 0.00067601 | 0.00048343 | 0.0025526 | 21.0387 | 2.838% | 24.918 | 0.0016383 | 0.00078204 | 0.00056094 | 0.0029813 | 21.0004 | -0.1822% | 24.8594 | 0.0016219 | 0.00077504 | 0.0005558 | 0.0029527 | 21.0007 | 0.001607% | 24.8599 | 0.001622 | 0.00077511 | 0.00055585 | 0.002953 | 21.0007 | 1e-06% | 24.8599 | 0.001622 | 0.00077511 | 0.00055585 | 0.002953 | 21.0007 | -5.532e-12% | 24.8599 | 0.001622 | 0.00077511 | 0.00055585 | 0.002953 | 21.0007 | 1.692e-14% | 24.8599 | 0.001622 | 0.00077511 | 0.00055585 | 0.002953 | 21.0007 | 0% | 24.8599 | 0.001622 | 0.00077511 | 0.00055585 | 0.002953 | 21.0007 | 0% | 0.99983 | 595.8997 | 24.8599 | 0.001622 | 0.00077511 | 0.00055585 | 0.002953 | 595.7984 | 8943.9368 | 54.93% | 0.016283 | 61.4141 | 209.5451 | 8.344 | 1071.9021 | 252.1644 |  | Calories per Btu |  | calculated |  | 16.7567 | 8.3158 | 0.5 | 1437.2173 | 1169.4339 | 71707.9135 | 267.7833
Oct | 31 | 9.4882 | 5.7108 | 10.1199 | 9.3738 | 0.5 | 14.8575 |  | 53.4718 | 182.4456 | 4.7376 | 6.3488 | 0.0014123 | 0.002953 | 47.82% | 0% |  | 51.6% |  | 0.002953 | 9.1602 | 6.6718 | 4.1907 | 2.47 | 0 | 0.12 | 4.5775 | 5.298e-07 | 0.9997 | 590.3847 | 12.3697 | 1408.2114 | 1604.3529 | 0% | 14.8575 | 14.2783 | 16.2658 | 0.0012183 | 0.0008427 | 0.00050811 | 0.0025691 | 14.8997 | 4.352% | 16.9321 | 0.0014266 | 0.00096862 | 0.00058596 | 0.0029812 | 14.8571 | -0.2858% | 16.8857 | 0.0014121 | 0.00095999 | 0.00058061 | 0.0029527 | 14.8575 | 0.002532% | 16.8861 | 0.0014123 | 0.00096007 | 0.00058065 | 0.002953 | 14.8575 | 1.646e-06% | 16.8861 | 0.0014123 | 0.00096007 | 0.00058065 | 0.002953 | 14.8575 | -9.517e-12% | 16.8861 | 0.0014123 | 0.00096007 | 0.00058065 | 0.002953 | 14.8575 | 0% | 16.8861 | 0.0014123 | 0.00096007 | 0.00058065 | 0.002953 | 14.8575 | 0% | 16.8861 | 0.0014123 | 0.00096007 | 0.00058065 | 0.002953 | 14.8575 | 0% | 0.99983 | 595.8997 | 16.8861 | 0.0014123 | 0.00096007 | 0.00058065 | 0.002953 | 595.7984 | 8943.9366 | 47.82% | 0.018701 | 53.4718 | 182.4456 | 8.344 | 1071.9021 | [6 empty] | 10.1199 | 9.3738 | 0.5 | 1604.3529 | 1301.1803 | 91913.6435 | 303.1726
Nov | 30 | 3.5227 | 0.83237 | 5.0595 | 10.5587 | 0.5 | 10.0181 |  | 47.208 | 161.0737 | 4.9586 | 5.4243 | 0.0012468 | 0.002953 | 42.22% | 0% |  | Condenser duty (heat added to surface water) as percent of fuel heat |  | 0.002953 | 6.4871 | 4.7247 | 4.7204 | 2.47 | 0 | 0.12 | 5.1439 | 5.9536e-07 | 0.99992 | 593.1426 | 8.7546 | 1530.3684 | 1679.1921 | 0% | 10.0181 | 9.5786 | 11.9286 | 0.0011208 | 0.0010294 | 0.00052434 | 0.0026745 | 10.0493 | 4.913% | 12.3113 | 0.0012559 | 0.0011366 | 0.00058042 | 0.0029729 | 10.0179 | -0.3121% | 12.2855 | 0.0012468 | 0.0011294 | 0.00057667 | 0.0029529 | 10.0181 | 0.001972% | 12.2856 | 0.0012468 | 0.0011295 | 0.00057669 | 0.002953 | 10.0181 | 8.882e-07% | 12.2856 | 0.0012468 | 0.0011295 | 0.00057669 | 0.002953 | 10.0181 | -2.518e-12% | 12.2856 | 0.0012468 | 0.0011295 | 0.00057669 | 0.002953 | 10.0181 | 5.319e-14% | 12.2856 | 0.0012468 | 0.0011295 | 0.00057669 | 0.002953 | 10.0181 | 0% | 12.2856 | 0.0012468 | 0.0011295 | 0.00057669 | 0.002953 | 10.0181 | 0% | 0.99983 | 595.8997 | 12.2856 | 0.0012468 | 0.0011295 | 0.00057669 | 0.002953 | 595.7984 | 8943.9366 | 42.22% | 0.021183 | 47.208 | 161.0737 | 8.344 | 1071.9021 | [6 empty] | 5.0595 | 10.5587 | 0.5 | 1679.1921 | 1361.3018 | 101054.2343 | 317.8903
Dec | 31 | -2.6297 | -5.4898 | 0.89876 | 10.5927 | 0.5 | 6.3718 |  | 41.3417 | 141.0578 | 5.473 | 4.9086 | 0.0010919 | 0.002953 | 36.98% | 0% |  |  |  | 0.002953 | 4.0617 | 2.2017 | 4.7356 | 2.47 | 0 | 0.12 | 5.1612 | 5.9736e-07 | 0.99987 | 595.4102 | 6.5183 | 1724.5253 | 1853.3982 | 0% | 6.3718 | 5.9912 | 9.3398 | 0.0010034 | 0.0011638 | 0.00056673 | 0.0027339 | 6.3993 | 6.811% | 9.6068 | 0.0010984 | 0.001257 | 0.0006135 | 0.0029689 | 6.3717 | -0.4317% | 9.5885 | 0.0010919 | 0.0012507 | 0.00061033 | 0.0029529 | 6.3718 | 0.002205% | 9.5886 | 0.0010919 | 0.0012507 | 0.00061035 | 0.002953 | 6.3718 | 8.153e-07% | 9.5886 | 0.0010919 | 0.0012507 | 0.00061035 | 0.002953 | 6.3718 | -1.519e-12% | 9.5886 | 0.0010919 | 0.0012507 | 0.00061035 | 0.002953 | 6.3718 | -1.394e-14% | 9.5886 | 0.0010919 | 0.0012507 | 0.00061035 | 0.002953 | 6.3718 | 0% | 9.5886 | 0.0010919 | 0.0012507 | 0.00061035 | 0.002953 | 6.3718 | 0% | 0.99983 | 595.8997 | 9.5886 | 0.0010919 | 0.0012507 | 0.00061035 | 0.002953 | 595.7984 | 8943.9363 | 36.98% | 0.024189 | 41.3417 | 141.0578 | 8.344 | 1071.9021 | [6 empty] | 0.89876 | 10.5927 | 0.5 | 1853.3982 | 1519.684 | 111365.2189 | 333.7143
|  | Input values in purple | [18 empty] | Lowe 1977 below 62.276 deg C, my ad hoc cubic above that | [7 empty] | Ward, 1980 | Ward, 1980 | Lowe 1977 below 62.276, my ad hoc cubic above that
1.0857
| The author gratefully acknowledges the assistance of David I. Stannard | [16 empty] | Annual mean forced evaporation (L/KWhe)
[22 empty] | from http://www.wrh.noaa.gov/slc/projects/wxcalc/formulas/rhTdFromWetBulb.pdf | [13 empty] | error in intial guess
-4.756%
-6.781%
-4.721%
-3.418%
-3.307%
-2.61%
-1.837%
-1.772%
-2.584%
-3.898%
-4.387%
-5.973%

## Read Me
Model of Forced Evaporation from a Water Surface (FEWS), with choice of wind function
Version 3.104 - 2013/09/24 - Timothy H. Diehl
ABSTRACT
This spreadsheet implements methods described in Diehl and others ( 2013) for estimating forced evaporation from water surfaces driven by heat from thermoelectric power plants.
The spreadsheet is used by entering input data; calculations are automatic:
1. The user enters power-plant characteristics and mean monthly air temperature, wet bulb temperature, and wind speed are acquired for the site being modeled and entered.
2. A natural water temperature is derived from measured river temperature upstream from the plant, or in nearby lakes and streams, and entered. In principle, a natural water temperature could be derived from air temperature and wet bulb temperature.
3. A heat loading (heat added to surface-water per pond or plume area) is estimated or measured and entered.
4. An appropriate wind function is selected and its coefficients are entered.
5. The spreadsheet solves the relevant heat-loss equations iteratively to estimate a heated water temperature that matches the heat loading.
6. Monthly and annual estimates of forced evaporation are calculated as functions of added heat.
The method implemented in this spreadsheet has four major sources of uncertainty:
1. The estimation of a natural water temperature in the absence of added heat;
2. The estimation of heat loading in a lake or river plume;
3. The selection of a wind function, and
4. At most 10-15-percent error between calculations and real heat loss (Stannard, D.I., USGS, written commun., 2012).
Forced evaporation in natural surface-water bodies occurs outside the power-plant boundary and cannot be easily measured. Forced evaporation from dedicated cooling ponds can be measured using water budgets, and could be used to test this spreadsheet.
This spreadsheet includes wind functions derived for rivers and lakes and reviewed by McJannet and others (2012), and the wind function of Brady and others (1969) developed for dedicated cooling lakes. Majewski and Miller (1979) reviewed other wind functions, but these should be checked against the original publications before being used. Other wind functions can be added by the user as appropriate.
NOTES
The first tab, "Forced Evaporation" stands on its own and is the only tab needed to apply the method.
INPUT SECTION
C6. "Input values in purple" means that all numbers in purple on a light purple background are intended to be changed by the user. Other numbers are functions or constants, and altering them may cause miscalculations.
A9. Most constants are given in columns DO - DY, others in DG1-DJ7. This spreadsheet applies the method developed by Earl Harbeck as documented by George Ward (1980).
B11. This method was originally designed to be applied to monthly data. Conversion to a shorter time step is probably not realistic.
C11-D23. We used NOAA weather data.
E12-E23. The natural or upstream water temperature is a critical input but it is difficult to estimate accurately from existing data.
G12. The monthly average heat loading is an important input. The added heat can be calculated by dividing the monthly fuel consumption in thermal megawatt-hours by the number of hours in the month, then multiplying by the percentage in cell S21. For dedicated cooling ponds, the area in question is that of the pond; for plants that create a thermal plume in a river or large lake, the appropriate area is the area over which the average temperature increase is equal to the estimated heating in cells L12-L23
Added heat loading is less than 0.5 MWt/acre for most lakes and rivers, but could be as high as 2 for some dedicated cooling ponds. A value in this cell will be copied into G13-G23. However, the user can provide monthly heat loadings. The added heat load is shown in different units in column U.
WIND FUNCTIONS
The "wind function" has been used to calibrate energy budgets, and as such, it accumulates all the unexplained variation. It's informative to look at the original studies to see how much scatter there is around these curves.
H7-J7. Copy numbers from Q2-S8 into these cells.
I use the function of Brady and others for dedicated cooling ponds and lakes, Gulliver and Stefan for rivers, and Webster and Sherman for large lakes.
SUMMARY OUTPUT
H12-H23. Estimated average water-surface temperature in the heated plume or cooling pond. Estimated temperatures above the boiling point won't be displayed.
I12-I23. An asterisk in this column indicates that the estimate should not be trusted. This column will remain blank until heated water temperature exceeds 50 degrees Celsius, which is an unrealistically high temperature for a cooling pond, and the temperature at which the accuracy of some of the fundamental functions in the method begins to decline.
J12-J23. Estimated amount of forced evaporation, in gallons, per million British thermal units (Btu) added to the water. This estimate should be within 10-15 percent of the correct value if the natural water temperature and wind function are chosen correctly.
K12-K23. Estimated amount of forced evaporation, in gallons, per megawatt-hour of heat added to the water.
M12-M23. Estimated forced evaporation as a monthly depth.
P12-P23. Estimated heat loss through forced evaporation as a percentage of heat added by power plant.
Q12-Q23. Anything but zero in this column is a sign of non-convergence in the iterative solution. It's hard to get this without very unrealistic input values. Repeated in column AJ and calculated in column CX.
ANNUAL RESULTS
S18. An example value of the percentage of fuel heat exported from the plant as electricity.
S13. An example value of the percentage of fuel heat lost to the atmosphere. For a coal plant, this is normally 10-18 percent; for a nuclear plant, it is only 1-2 percent. In a plant with once-through or pond cooling with this spreadsheet, the value in this cell would have to include all the heat not discharged through the condenser or converted to electricity. If you wanted to model a plant with a cooling system including towers, this would include the heat lost to the atmosphere in the cooling towers, so it wouldn't be entirely "non-condenser" in that case.
S21. The fuel heat not exported as electricity or lost to the atmosphere is added to the cooling water.
R10. Assuming constant fuel use and electric production throughout the year, this is the average forced evaporation per MWh of heat added to the cooling water, It differs from the average of K12-K23 only because of differences in the length of months.
S10. Estimated forced evaporation per MWh of net electric production. This is the coefficient most often used to describe thermoelectric water consumption in English units. Compare to values given in Macknick and others (2011) table 2 for pond and once-through cooling, accessed at www.nrel.gov/docs/fy11osti/50900.pdf.
S26. Estimated forced evaporation in liters per KWh of net electric production.
T10. Annual depth of forced evaporation.
CALCULATIONS FOR UNHEATED CONDITION
V12-V23, AF12-AF23. See tab "Lowe 1977 e(T)" for supporting calculations.
W12-W23, See tab "unsaturated vapor pressure."
AD12-AD23, Ward's quadratic formula was sufficiently accurate, see tab "Ward Constants."
ITERATIVE SOLUTION
Columns AH and AL. This is an ad hoc approach to making a good intial guess at the heated water temperature. It assumes that the ratio of temperature change to added heat per acre is a quadratic function of initial temperature, windspeed, and added heat per area. It's crude but adequate, given that convergence is rapid and the final value is insensitive to the initial guess.
AI12-AI23. These final values are repeated here to allow comparison with the intitial guesses.
AN12-AO23. This is the first of nine applications of the basic equations for increased heat loss from the water surface as a result of added heat. See tab "Ward equation 1 2 3 14."
AQ12-AQ23. Estimated increase in heat loss due to raising the water temperature from the natural temperature (in column E) to the initial-guess heated water temperature (in column AL). This should approximate the heat loading given in columns G and U.
AS12-AS23. The estimated heated water temperature is adjusted to correct for the error in column AQ. Iterations continue through column DE.
OTHER SECTIONS
DG1-DG7. Conversion constants.
DG10-DN23. Conversion of evaporation to English units.
DP-DX. Constants, and air pressure as a function of elevation.
DZ-EP. Development of initial-guess quadratic.
SELECTED REFERENCES
Anderson, E.R., 1954, Energy budget studies, water-loss investigations: Lake Hefner Studies: U.S. Geological Survey Professional Paper 269, p. 71-119.
Brady, D.K., Graves, W.L., and Geyer, J.C., 1969, Surface heat exchange at power plant cooling lakes: New York, Edison Electric Institute Publication #69-901, Report #5. Also referenced as: The Johns Hopkins University, Baltimore, Maryland, USA, Research Project R-P-49, Report no. 5.
Butcher, K., Crown, L., and Gentry, E.J., 2006, The international system of units (SI) - conversion factors for general use: National Institute of Standards and Technology Special Publications 1038, 24 p, accessed September 10, 2012 at: http://www.nist.gov/pml/wmd/metric/upload/SP1038.pdf
Diehl, T.H., Harris, M.A., Murphy, J.C., and Hutson, S.S., 2013, Methods for estimating water consumption for thermoelectric power plants in the United States : U.S Geological Survey Scientific Investigations Report 2013-XXXX, xx p.
Diehl, T.H., 2011, Estimating forced evaporation from surface water, in Proceedings: Third Thermal Ecology and Regulation Workshop: October 11-12, 2011: Palo Alto, CA, EPRI, pp. 23-1--23-10.
Fulford, J.M., and Sturm, T.W., 1984, Evaporation from flowing channels: Journal of Energy Engineering, ASCE, v. 110, no. 1, p. 1-10.
Faqs.org, 1997, Temperature, humidity and dew point often needed answers. Accessed September 10, 2012 at:
http://www.faqs.org/faqs/meteorology/temp-dewpoint/
Gulliver, J.S., Stefan, H.G., 1986, Wind function for a sheltered stream: Journal of Environmental Engineering, v. 112, no. 2, p. 387-399.
Harbeck, G.E. Jr., 1964, Estimating forced evaporation from cooling ponds: Journal of the Power Division: Proceedings of the American Society of Civil Engineers, v. 90, no. 3, p. 1-10.
Lowe, P.R., 1977, An approximating polynomial for the computation of saturation vapor pressure: Journal of Applied Meteorology, v. 16, p. 100 - 102.
Macknick, J., Newmark, R., Heath, G., and Hallett, K.C., 2011, A review of operational water consumption and withdrawal factors in electricity generating technologies: Golden, Colorado, National Renewable Energy Laboratory Technical report NREL/TP—6A20-50900, 21 p., accessed August 19, 2013 at http://www.nrel.gov/docs/fy11osti/50900.pdf.
Majewski, W., and Miller, D.C., 1979, Predicting effects of power plant once-through cooling on aquatic systems: A state-of-the-art report of IHP Working Group 6.2 on the Effects of Thermal Discharges.: Paris, France: UNESCO, Technical papers in hydrology 20, 171 p.
McJannet, D.L., Webster, I.T., and Cook, F.J., 2012, An area-dependent wind function for estimating open water evaporation using land-based meteorological data: Environmental Modelling & Software, v, 31, p. 76-83, http://dx.doi.org/10.1016/j.envsoft.2011.11.017, accessed July 30, 2013 at http://www.sciencedirect.com/science/article/pii/S1364815211002805.
National Oceanic and Atmospheric Administration, 2012, Relative humidity and dewpoint temperature from temperature and wet-bulb temperature, accessed September 10, 2012 at
http://www.wrh.noaa.gov/slc/projects/wxcalc/formulas/rhTdFromWetBulb.pdf
Oklahoma State University, 2001, Vapor pressure of water, accessed September 10, 2012 at
http://intro.chem.okstate.edu/1515sp01/database/vpwater.html
Portland State Aerospace Society, 2004, A quick derivation relating altitude to air pressure. Version 1.03, 12/22/2004, accessed September 10, 2012 at
http://psas.pdx.edu/RocketScience/PressureAltitude_Derived.pdf
The Engineering ToolBox, 2012, Water - thermal properties, accessed September 10, 2012 at
http://www.engineeringtoolbox.com/water-thermal-properties-d_162.html
The Engineering ToolBox, 2012, Air pressure and altitude above sea level, accessed September 10, 2012 at
http://www.engineeringtoolbox.com/air-altitude-pressure-d_462.html
Ward, G.H., Jr., 1980, Accuracy of Harbeck diagram for forced evaporation: Journal of the Energy Division, v. 106, no. 1, p. 23-31.
Webster, I.T., and Sherman, B.S., 1995, Evaporation from fetch-limited water bodies: Irrigation Science, v. 16, p. 53-64.

## Glossary of label cells
Label on "Forced Evaporation" tab | Explanation
Dry bulb air temperature Ta (oC) | degrees Celsius
Wet bulb air temperature Twb (oC) | degrees Celsius
Natural water temperature T (oC) | degrees Celsius
Wind speed at 2m W (mph) | Wind speed at 2 meters above the surface, in miles per hour
Added heat load rH (MW/acre) | Heat added to a surface-water body by a power plant, in thermal megawatts per acre
Heated water temperature T' (oC) | degrees Celsius
Asterisk indicates declining precision at T' > 50 | Asterisk indicates declining precision at heated water temperature above 50 degrees Celsius
Evaporated gallons per million Btu of condenser duty | Btu are British Thermal Units
Evaporated gallons per MWh thermal condenser duty | Gallons of surface water evaporated per megawatt-hour of heat transferred to it from the condenser
Heating of water (oC) | Change in water temperature from natural water temperature to heated water temperature.
Added evaporation (cm/ month) | Increased evaporation in excess of natural evaporation, in centimeters per month
Evaporative heat loss increment | Heat transferred to the atmosphere through evaporation from surface water, in calories per square centimeter of water surface per second
Total heat loss increment | Heat transferred to the atmosphere through evaporation, conduction, and radiation from surface water, in calories per square centimeter of water surface per second
Evaporative cooling as percent of added heat | This is calculated as the ratio of evaporative heat loss increment to total heat loss increment
Percent change in T' in last iteration | This has no physical interpretation; it tracks the convergence of the heated water temperature through the iterations
Annual mean forced evaporation (gal/ MWht condenser duty) | Annual average rate of forced evaporation in gallons per thermal megawatt-hour of added heat
Annual mean forced evaporation (gal/Mwe) | Annual average rate of forced evaporation in gallons per megawatt-hour of net electrical generation
Added evaporation (cm) | Annual sum of monthly forced evaporation, in centimeters of water depth over the actual or assumed surface-water area
input heat load, cal/(cm2 sec) | Heat added to a surface-water body by a power plant, in thermal megawatts per acre
e(Twb) in mbar | Vapor pressure of water at the wet-bulb air temperature, in millibars
ea in mbar | Vapor pressure of water at the dry-bulb air temperature, in millibars
windspeed in m/s | Wind speed at 2 meters above the surface, in meters per second
a | Wind-function coefficients
b
c
f(W) in mm/ (day*kPa) | Calculated wind function in millimeters per day per kilopascal
f(W) in cm/(sec*mbar) | Calculated wind function in centimeters of water per second per millibar
ρ (g/cm3) | Density of water, in grams per cubic centimeter
L (cal/g) | Heat of vaporization of liquid water, in calories per gram
e(T) (mbar) | Saturation vapor pressure at natural water temperature, in millibars
initial estimated ratio of delta T to heat loading | Initial guess used to start iteration; delta T is T' minus T, and heat loading is in calories per square centimeter of water surface per second
Percent change in T' in last iteration | Change in heated water temperature in final iteration step; if the method converged successfully, this should be small.

## Ward equation 1 2 3 14
Ward 1980 equations 1, 2, 3, and 14
Ward 1980 eqn number |  | natural | heated
1 | E = ρ Lf(W)[e(T) - ea] | 0.0062523 | 0.0081595 | evaporation | 0.0019071 | evap increment
2 | C=f(W)ρpCp(T- Ta)/ϵ | 0.00053873 | 0.0010771 | conduction | 0.00053841 | conduction increment
3 | R = ϵrσ(T + 273)^4 | 0.010936 | 0.011081 | radiation | 0.00014556 | radiation inrement
| sigma in "per day" | 86400 |  |  | 0.0025911 | total increment
[5 empty] | 73.6% | evap ratio
14 | f(W) = 7E-8*W | 1.4e-06
| f(W) in "per second" units | 1
ρ | 0.996 | g/cm3 | 0.99571
p | 1001.3018 | in mbars
ϵr | 0.97 | per day |  |  |  |  | 0.0062523 | 0.0081595 | 0.0019071 | evap increment
σ | 1.171e-07 | cal/(cm2 • K4 • day) |  |  |  |  | 0.00053873 | 0.0010771 | 0.00053841 | conduction increment
Rν | 0.11 | cal/(g • K) |  |  |  |  | 0.010936 | 0.011081 | 0.00014556 | radiation inrement
L | 580 | cal/g | 579.55 | [5 empty] | 0.0025911 | total increment
cp | 0.24 | cal/(g • K) | [6 empty] | 73.6% | forced evaporation ratio
ϵ | 0.622 | [5 empty] | 0.086165 | 0.13201 | ratio of conduction to evaporation heat, Ward
Ta | 28 | dry bulb air T
Twb | 26 | wet bulb air T
T | 29 | natural water T | 30 | heated water T
W | 20 | wind at 2m in mph
e(T) | 39.9921 | mb | 42.361 | mb
e(Twb) | 33.6224 | mb
ea | 32.2612 | mb
e = 6.1078 * 10 ** ((TD * A)/(TD + B)) in hPa
A = 7.5 } for use in vapor pressure
B = 237.3 } with respect to WATER
http://www.faqs.org/faqs/meteorology/temp-dewpoint/

## altitude vs. air pressure
This formula is used in the model:
A Quick Derivation relating altitude to air pressure
Version 1.03, 12/22/2004
© 2004 Portland State Aerospace Society <http://www.psas.pdx.edu>
pages 3 to 4:
"The 1996 edition of the CRC handbook gives this expression for pressure in terms of altitude in the standard atmosphere"
source url: http://psas.pdx.edu/RocketScience/PressureAltitude_Derived.pdf
| P=100 * ((44331.514 - z)/11880.516)^(1/0.190263) |  |  |  |  | P = pressure in Pascals
z = altitude in meters
| Input | 100 | elevation in meters
| p | 1001.3018 | in mbars
Alternative formula:
Engineering Toolbox
http://www.engineeringtoolbox.com/air-altitude-pressure-d_462.html
Air pressure above sea level can be calculated as
p = 101325 (1 - 2.25577 10-5 h)5.25588 (1)
where
p = air pressure (Pa)
h = altitude above sea level (m)
| 100129.4375 | Pa
difference from CRC formula
-0.0007459%
1001.2944
A second alternative formula:
| z = 44330.8 - 4946.54*(p^0.1902632) |  |  |  | Portland State prefers slightly different parameters
| (p^0.1902632) = (44330.8-z)/4946.54 |  |  |  | The differences among these three equations are insignificant for the purpose of this model.
p = ((44330.8-z)/4946.54)^(1/0.1902632)
|  | 100129.9026 | Pa
|  | 1001.299 | mbar | -0.0002814% | difference from CRC formula |  | 0.0004645% | difference from Engineering Toolbox formula

## Lowe 1977 e(T)
Lowe, P.R., 1977, An approximating polynomial for the computation of saturation vapor pressure. Journal of Applied Meteorology, v. 16, p. 100 - 102
|  | Compared to Ward's (1980) formula and a table of e(T) from the Oklahoma State University Chemistry Department. | [6 empty] | http://intro.chem.okstate.edu/1515sp01/database/vpwater.html
E = a0+T(a1+T(a2+T(a3+T(a4+T(a5+a6T))))) | [5 empty] | See separate tab "Ward Eqn 12" for this equation |  |  | Temperature | Pressure | mb | [5 empty] | -296.9012 | Change |  |  | -303.6283 | -303.9609 | -301.5852 | -296.9012
subscript | a |  |  |  |  | Ward 1980 equation 12 |  |  | 0 | 4.6 | 6.1328 | [5 empty] | 16.9016 | these |  |  | 17.1781 | 17.1955 | 17.101 | 16.9016
0 | 6.1078 |  |  |  |  | a | 595.9 |  | 1 | 4.9 | 6.5328 | [5 empty] | -0.30224 | with |  |  | -0.30594 | -0.30622 | -0.305 | -0.30224
1 | 0.44365 |  |  |  |  | b | -0.545 |  | 2 | 5.3 | 7.0661 | [5 empty] | 0.0026412 | Solver…. |  |  | 0.0026573 | 0.0026587 | 0.0026536 | 0.0026412
2 | 0.014289 |  |  |  |  | Rν | 0.11 |  | 3 | 5.7 | 7.5994 | [5 empty] | RMSE |  |  |  | RMSE | RMSE | RMSE | RMSE
3 | 0.00026506 |  |  |  |  | T | 29 |  | 4 | 6.1 | 8.1327 | [5 empty] | 0.44681 |  |  |  | 0.44766 | 0.44794 | 0.44738 | 0.44681
4 | 3.0312e-06 |  |  |  |  | e(T) | 40.0708 |  | 5 | 6.5 | 8.666 | [5 empty] | ….to minimize this
5 | 2.0341e-08 | [7 empty] | 6 | 7 | 9.3326 |  | The purpose of my cubic equation is to provide a fairly good fit to the Oklahoma State table at high temperatures where the Lowe equation goes astray. I don't think these temperatures actually occur in cooling ponds.
6 | 6.1368e-11 | [7 empty] | 7 | 7.5 | 9.9992
33 |  | 50.3053 | [6 empty] | 8 | 8 | 10.6658 |  | http://intro.chem.okstate.edu/1515sp01/database/vpwater.html
T Celsius | Goff & Gratch 1946 from Lowe 1977 | Lowe | Lowe results | Lowe % change from Goff-Gratch | Lowe error as % of Ward error | Ward | Ward % change from Lowe | Ward % change from Goff-Gratch | 9 | 8.6 | 11.4657 |  | Temperature | Pressure | mb |  | my cubic equation | squared error in cubic | error | Lowe error | Crossover difference | combined equation
0 | 6.1078 | 6.1078 | 6.1078 | -6.385e-07% | infinite | 6.1078 | 6.385e-07% | 0% | 10 | 9.2 | 12.2657
5 | 8.7192 | 8.7184 | 8.7184 | -0.009544% | -77.55% | 8.7203 | 0.02185% | 0.01231% | 11 | 9.8 | 13.0656
10 | 12.2723 | 12.2707 | 12.2707 | -0.01274% | -53.66% | 12.2752 | 0.03648% | 0.02374% | 12 | 10.5 | 13.9988 |  | 40 | 55.3 | 73.7273 |  | 64.6145 |  | -12.36% | -0.009544% |  | 73.7754
15 | 17.0438 | 17.0419 | 17.0419 | -0.01114% | -33.51% | 17.0495 | 0.04439% | 0.03324% | 13 | 11.2 | 14.9321 |  | 41 | 58.3 | 77.7269 |  | 70.032 |  | -9.9% | -0.01274% |  | 77.8003
20 | 23.373 | 23.3712 | 23.3712 | -0.007891% | -20.06% | 23.3822 | 0.04724% | 0.03935% | 14 | 12 | 15.9987 |  | 42 | 61.5 | 81.9933 |  | 75.4948 |  | -7.926% | -0.01114% |  | 82.0134
25 | 31.6709 | 31.6693 | 31.6693 | -0.004903% | -11.82% | 31.684 | 0.04639% | 0.04149% | 15 | 12.8 | 17.0653 |  | 43 | 64.8 | 86.3929 |  | 81.0187 |  | -6.221% | -0.007891% |  | 86.422
30 | 42.4304 | 42.4289 | 42.4289 | -0.003435% | -8.882% | 42.4468 | 0.04211% | 0.03867% | 16 | 13.6 | 18.1318 |  | 44 | 68.3 | 91.0592 |  | 86.6195 |  | -4.876% | -0.004903% |  | 91.0334
35 | 56.2366 | 56.2348 | 56.2348 | -0.003272% | -10.89% | 56.2535 | 0.03333% | 0.03006% | 17 | 14.5 | 19.3317 |  | 45 | 71.9 | 95.8588 |  | 92.3132 |  | -3.699% | -0.003435% |  | 95.8553
40 | 73.7775 | 73.7754 | 73.7754 | -0.002852% | -19.15% | 73.7885 | 0.01775% | 0.01489% | 18 | 15.5 | 20.665 |  | 46 | 75.7 | 100.925 |  | 98.1155 |  | -2.784% | -0.003272% |  | 100.8958
45 | 95.8548 | 95.8553 | 95.8553 | 0.0005622% | -7.549% | 95.8477 | -0.008009% | -0.007446% | 19 | 16.5 | 21.9982 |  | 47 | 79.6 | 106.1246 |  | 104.0423 |  | -1.962% | -0.002852% |  | 106.1627
50 | 123.4 | 123.4078 | 123.4078 | 0.006303% | -15.1% | 123.3485 | -0.04803% | -0.04173% | 20 | 17.5 | 23.3314 |  | 48 | 83.7 | 111.5908 |  | 110.1094 |  | -1.328% | 0.0005622% |  | 111.6646
| http://intro.chem.okstate.edu/1515sp01/database/vpwater.html | Matches Lowe results exactly |  | Lowe change from ok.state table |  |  |  |  | 21 | 18.7 | 24.9313 |  | 49 | 88 | 117.3237 |  | 116.3327 | 0.982 | -0.8446% | 0.006303% |  | 117.41
51 | 129.5893 | 129.6669 |  | 0.05988% |  | 129.5915 | -0.05814% |  | 22 | 19.8 | 26.3978 |  | 50 | 92.5 | 123.3232 |  | 122.7281 | 0.35414 | -0.4826% | 0.05988% |  | 123.4078
52 | 136.1221 | 136.1968 |  | 0.05488% |  | 136.1028 | -0.06904% |  | 23 | 21.1 | 28.131 |  | 51 | 97.2 | 129.5893 |  | 129.3113 | 0.077281 | -0.2145% | 0.05488% |  | 129.6669
53 | 142.9216 | 143.0071 |  | 0.05981% |  | 142.8915 | -0.08077% |  | 24 | 22.4 | 29.8642 |  | 52 | 102.1 | 136.1221 |  | 136.0983 | 0.00056652 | -0.01749% | 0.05981% |  | 136.1968
54 | 149.9877 | 150.1074 |  | 0.07986% |  | 149.9673 | -0.09337% |  | 25 | 23.8 | 31.7307 |  | 53 | 107.2 | 142.9216 |  | 143.1049 | 0.033609 | 0.1283% | 0.07986% |  | 143.0071
55 | 157.3204 | 157.5081 |  | 0.1193% |  | 157.3398 | -0.1069% |  | 26 | 25.2 | 33.5972 |  | 54 | 112.5 | 149.9877 |  | 150.3469 | 0.12906 | 0.2395% | 0.1193% |  | 150.1074
56 | 165.0531 | 165.2194 |  | 0.1007% |  | 165.0189 | -0.1213% |  | 27 | 26.7 | 35.5971 |  | 55 | 118 | 157.3204 |  | 157.8402 | 0.27018 | 0.3304% | 0.1007% |  | 157.5081
57 | 173.0524 | 173.252 |  | 0.1153% |  | 173.015 | -0.1367% |  | 28 | 28.3 | 37.7302 |  | 56 | 123.8 | 165.0531 |  | 165.6006 | 0.29975 | 0.3317% | 0.1153% |  | 165.2194
58 | 181.4517 | 181.6167 |  | 0.09093% |  | 181.3385 | -0.1532% |  | 29 | 30 | 39.9967 |  | 57 | 129.8 | 173.0524 |  | 173.644 | 0.3499 | 0.3418% | 0.09093% |  | 173.252
59 | 190.1177 | 190.3249 |  | 0.109% |  | 190 | -0.1707% |  | 30 | 31.8 | 42.3965 |  | 58 | 136.1 | 181.4517 |  | 181.9862 | 0.28559 | 0.2945% | 0.109% |  | 181.6167
60 | 199.1836 | 199.3881 |  | 0.1026% |  | 199.0106 | -0.1893% |  | 31 | 33.7 | 44.9296 |  | 59 | 142.6 | 190.1177 | 190.3249 | 190.643 | 0.27596 | 0.2763% | 0.1026% | -0.31808 | 190.3249 | 0 | -0.31808
61 | 208.5162 | 208.8179 |  | 0.1447% |  | 208.3814 | -0.209% |  | 32 | 35.7 | 47.5961 |  | 60 | 149.4 | 199.1836 | 199.3881 | 199.6304 | 0.1996 | 0.2243% | 0.1447% | -0.24233 | 199.3881 | 0 | -0.24233
62 | 218.382 | 218.6265 |  | 0.1119% |  | 218.1238 | -0.2299% |  | 33 | 37.7 | 50.2625 |  | 61 | 156.4 | 208.5162 | 208.8179 | 208.9641 | 0.20065 | 0.2148% | 0.1119% | -0.14624 | 208.8179 | 0 | -0.14624
63 | 228.5145 | 228.8263 |  | 0.1364% |  | 228.2496 | -0.2521% |  | 34 | 39.9 | 53.1956 |  | 62.27 |  |  | 221.3414 | 221.3421 |  |  |  | -0.00074475 | 221.3414 | 0 | -0.00074475
64 | 239.047 | 239.43 |  | 0.1602% |  | 238.7706 | -0.2754% |  | 35 | 42.2 | 56.262 |  | 62.271 |  |  | 221.3515 | 221.3521 |  |  |  | -0.00062152 | 221.3515 | 0 | -0.00062152
65 | 249.9794 | 250.4507 |  | 0.1885% |  | 249.6992 | -0.3% |  | 36 | 44.6 | 59.4618 |  | 62.272 |  |  | 221.3616 | 221.3621 |  |  |  | -0.00049828 | 221.3616 | 0 | -0.00049828
66 | 261.4452 | 261.9016 |  | 0.1746% |  | 261.0478 | -0.326% |  | 37 | 47.1 | 62.7948 |  | 62.273 |  |  | 221.3717 | 221.3721 |  |  |  | -0.00037503 | 221.3717 | 0 | -0.00037503
67 | 273.3109 | 273.7963 |  | 0.1776% |  | 272.829 | -0.3533% |  | 38 | 49.7 | 66.2612 |  | 62.274 |  |  | 221.3818 | 221.3821 |  |  |  | -0.00025176 | 221.3818 | 0 | -0.00025176
68 | 285.5765 | 286.149 |  | 0.2005% |  | 285.056 | -0.382% |  | 39 | 52.4 | 69.8609 |  | 62.275 |  |  | 221.3919 | 221.3921 |  |  |  | -0.00012848 | 221.3919 | 0 | -0.00012848
69 | 298.2421 | 298.974 |  | 0.2454% |  | 297.7419 | -0.4121% |  | 40 | 55.3 | 73.7273 |  | 62.276 |  |  | 221.402 | 221.402 |  |  |  | -5.1942e-06 | 221.402 | 5.1942e-06 | -5.6843e-13
70 | 311.5744 | 312.2858 |  | 0.2283% |  | 310.9003 | -0.4437% |  | 41 | 58.3 | 77.7269 |  | 62.277 |  |  | 221.4121 | 221.412 |  |  |  | 0.00011811 | 221.412 | -0.00011811 | -5.6843e-13
71 | 325.1733 | 326.0995 |  | 0.2849% |  | 324.545 | -0.4767% |  | 42 | 61.5 | 81.9933 |  | 62.278 |  |  | 221.4223 | 221.422 |  |  |  | 0.00024142 | 221.422 | -0.00024142 | -4.5475e-13
72 | 339.4387 | 340.4306 |  | 0.2922% |  | 338.69 | -0.5113% |  | 43 | 64.8 | 86.3929 |  | 62.279 |  |  | 221.4324 | 221.432 |  |  |  | 0.00036475 | 221.432 | -0.00036475 | -5.6843e-13
73 | 354.2375 | 355.2946 |  | 0.2984% |  | 353.3498 | -0.5474% |  | 44 | 68.3 | 91.0592 |  | 62.28 |  |  | 221.4425 | 221.442 |  |  |  | 0.00048809 | 221.442 | -0.00048809 | -3.4106e-13
74 | 369.5696 | 370.7077 |  | 0.308% |  | 368.5388 | -0.5851% |  | 45 | 71.9 | 95.8588 |  | 62.281 |  |  | 221.4526 | 221.452 |  |  |  | 0.00061144 | 221.452 | -0.00061144 | -5.6843e-13
75 | 385.435 | 386.6864 |  | 0.3247% |  | 384.272 | -0.6244% |  | 46 | 75.7 | 100.925 |  | 62.282 |  |  | 221.4627 | 221.462 |  |  |  | 0.0007348 | 221.462 | -0.0007348 | -2.2737e-13
76 | 401.8336 | 403.2474 |  | 0.3518% |  | 400.5645 | -0.6653% |  | 47 | 79.6 | 106.1246 |  | 62.283 |  |  | 221.4728 | 221.472 |  |  |  | 0.00085818 | 221.472 | -0.00085818 | -2.2737e-13
77 | 418.7656 | 420.408 |  | 0.3922% |  | 417.4319 | -0.7079% |  | 48 | 83.7 | 111.5908 |  | 62 | 163.8 | 218.382 | 218.6265 | 218.6601 | 0.077297 | 0.1273% | 0.1364% | -0.033558 | 218.6265 | 0 | -0.033558
78 | 436.3641 | 438.1859 |  | 0.4175% |  | 434.8897 | -0.7522% |  | 49 | 88 | 117.3237 |  | 63 | 171.4 | 228.5145 | 228.8263 | 228.7341 | 0.048191 | 0.09607% | 0.1602% | 0.092262 | 228.7341 | -0.092262 | -5.6843e-13
79 | 454.6293 | 456.5988 |  | 0.4332% |  | 452.954 | -0.7983% |  | 50 | 92.5 | 123.3232 |  | 64 | 179.3 | 239.047 |  | 239.202 | 0.024013 | 0.06482% | 0.1885% |  | 239.202
80 | 473.4277 | 475.6654 |  | 0.4726% |  | 471.6411 | -0.846% |  | 51 | 97.2 | 129.5893 |  | 65 | 187.5 | 249.9794 |  | 250.0796 | 0.010036 | 0.04008% | 0.1746% |  | 250.0796
81 | 492.8928 | 495.4042 |  | 0.5095% |  | 490.9675 | -0.8956% |  | 52 | 102.1 | 136.1221 |  | 66 | 196.1 | 261.4452 |  | 261.3829 | 0.0038802 | -0.02383% | 0.1776% |  | 261.3829
82 | 513.1578 | 515.8346 |  | 0.5216% |  | 510.9501 | -0.9469% |  | 53 | 107.2 | 142.9216 |  | 67 | 205 | 273.3109 |  | 273.1276 | 0.033593 | -0.06706% | 0.2005% |  | 273.1276
83 | 534.0894 | 536.9762 |  | 0.5405% |  | 531.606 | -1% |  | 54 | 112.5 | 149.9877 |  | 68 | 214.2 | 285.5765 |  | 285.3296 | 0.060984 | -0.08647% | 0.2454% |  | 285.3296
84 | 555.6876 | 558.849 |  | 0.5689% |  | 552.9526 | -1.055% |  | 55 | 118 | 157.3204 |  | 69 | 223.7 | 298.2421 |  | 298.0047 | 0.056378 | -0.07961% | 0.2283% |  | 298.0047
85 | 578.0858 | 581.4734 |  | 0.586% |  | 575.0076 | -1.112% |  | 56 | 123.8 | 165.0531 |  | 70 | 233.7 | 311.5744 |  | 311.1688 | 0.16448 | -0.1302% | 0.2849% |  | 311.1688
86 | 601.1506 | 604.8703 |  | 0.6188% |  | 597.789 | -1.171% |  | 57 | 129.8 | 173.0524 |  | 71 | 243.9 | 325.1733 |  | 324.8378 | 0.11255 | -0.1032% | 0.2922% |  | 324.8378
87 | 624.8819 | 629.0612 |  | 0.6688% |  | 621.315 | -1.231% |  | 58 | 136.1 | 181.4517 |  | 72 | 254.6 | 339.4387 |  | 339.0274 | 0.1692 | -0.1212% | 0.2984% |  | 339.0274
88 | 649.4133 | 654.0677 |  | 0.7167% |  | 645.6041 | -1.294% |  | 59 | 142.6 | 190.1177 |  | 73 | 265.7 | 354.2375 |  | 353.7536 | 0.2342 | -0.1366% | 0.308% |  | 353.7536
89 | 674.7445 | 679.9121 |  | 0.7659% |  | 670.6753 | -1.359% |  | 60 | 149.4 | 199.1836 |  | 74 | 277.2 | 369.5696 |  | 369.0321 | 0.28888 | -0.1454% | 0.3247% |  | 369.0321
90 | 701.009 | 706.6171 |  | 0.8% |  | 696.5476 | -1.425% |  | 61 | 156.4 | 208.5162 |  | 75 | 289.1 | 385.435 |  | 384.8789 | 0.3092 | -0.1443% | 0.3518% |  | 384.8789
91 | 727.9401 | 734.2058 |  | 0.8607% |  | 723.2403 | -1.494% |  | 62 | 163.8 | 218.382 |  | 76 | 301.4 | 401.8336 |  | 401.3098 | 0.27443 | -0.1304% | 0.3922% |  | 401.3098
92 | 755.9378 | 762.7019 |  | 0.8948% |  | 750.7733 | -1.564% |  | 63 | 171.4 | 228.5145 |  | 77 | 314.1 | 418.7656 |  | 418.3405 | 0.18066 | -0.1015% | 0.4175% |  | 418.3405
93 | 784.7355 | 792.1295 |  | 0.9422% |  | 779.1664 | -1.636% |  | 64 | 179.3 | 239.047 |  | 78 | 327.3 | 436.3641 |  | 435.9871 | 0.14217 | -0.08641% | 0.4332% |  | 435.9871
94 | 814.4663 | 822.5132 |  | 0.988% |  | 808.4399 | -1.711% |  | 65 | 187.5 | 249.9794 |  | 79 | 341 | 454.6293 |  | 454.2652 | 0.13255 | -0.08008% | 0.4726% |  | 454.2652
95 | 845.1305 | 853.8781 |  | 1.035% |  | 838.6143 | -1.788% |  | 66 | 196.1 | 261.4452 |  | 80 | 355.1 | 473.4277 |  | 473.1908 | 0.056128 | -0.05004% | 0.5095% |  | 473.1908
96 | 876.7279 | 886.2496 |  | 1.086% |  | 869.7105 | -1.866% |  | 67 | 205 | 273.3109 |  | 81 | 369.7 | 492.8928 |  | 492.7797 | 0.012782 | -0.02294% | 0.5216% |  | 492.7797
97 | 909.3919 | 919.6541 |  | 1.128% |  | 901.7495 | -1.947% |  | 68 | 214.2 | 285.5765 |  | 82 | 384.9 | 513.1578 |  | 513.0478 | 0.012095 | -0.02143% | 0.5405% |  | 513.0478
98 | 942.9891 | 954.1179 |  | 1.18% |  | 934.7527 | -2.03% |  | 69 | 223.7 | 298.2421 |  | 83 | 400.6 | 534.0894 |  | 534.0109 | 0.0061631 | -0.0147% | 0.5689% |  | 534.0109
99 | 977.5196 | 989.6682 |  | 1.243% |  | 968.7418 | -2.114% |  | 70 | 233.7 | 311.5744 |  | 84 | 416.8 | 555.6876 |  | 555.6848 | 7.7992e-06 | -0.0005026% | 0.586% |  | 555.6848
100 | 1013.25 | 1026.3328 |  | 1.291% |  | 1003.7387 | -2.201% |  | 71 | 243.9 | 325.1733 |  | 85 | 433.6 | 578.0858 |  | 578.0855 | 9.9027e-08 | -5.444e-05% | 0.6188% |  | 578.0855
[9 empty] | 72 | 254.6 | 339.4387 |  | 86 | 450.9 | 601.1506 |  | 601.2287 | 0.0060994 | 0.01299% | 0.6688% |  | 601.2287
[9 empty] | 73 | 265.7 | 354.2375 |  | 87 | 468.7 | 624.8819 |  | 625.1302 | 0.06165 | 0.03973% | 0.7167% |  | 625.1302
[9 empty] | 74 | 277.2 | 369.5696 |  | 88 | 487.1 | 649.4133 |  | 649.8061 | 0.15429 | 0.06049% | 0.7659% |  | 649.8061
[9 empty] | 75 | 289.1 | 385.435 |  | 89 | 506.1 | 674.7445 |  | 675.272 | 0.27821 | 0.07817% | 0.8% |  | 675.272
[9 empty] | 76 | 301.4 | 401.8336 |  | 90 | 525.8 | 701.009 |  | 701.5438 | 0.28601 | 0.07629% | 0.8607% |  | 701.5438
[9 empty] | 77 | 314.1 | 418.7656 |  | 91 | 546 | 727.9401 |  | 728.6374 | 0.48624 | 0.09579% |  |  | 728.6374
[9 empty] | 78 | 327.3 | 436.3641 |  | 92 | 567 | 755.9378 |  | 756.5687 | 0.398 | 0.08346% |  |  | 756.5687
[9 empty] | 79 | 341 | 454.6293 |  | 93 | 588.6 | 784.7355 |  | 785.3534 | 0.3819 | 0.07875% |  |  | 785.3534
[9 empty] | 80 | 355.1 | 473.4277 |  | 94 | 610.9 | 814.4663 |  | 815.0075 | 0.29285 | 0.06644% |  |  | 815.0075
[9 empty] | 81 | 369.7 | 492.8928 |  | 95 | 633.9 | 845.1305 |  | 845.5467 | 0.17327 | 0.04925% |  |  | 845.5467
[9 empty] | 82 | 384.9 | 513.1578 |  | 96 | 657.6 | 876.7279 |  | 876.987 | 0.06714 | 0.02955% |  |  | 876.987
[9 empty] | 83 | 400.6 | 534.0894 |  | 97 | 682.1 | 909.3919 |  | 909.3441 | 0.0022786 | -0.005249% |  |  | 909.3441
[9 empty] | 84 | 416.8 | 555.6876 |  | 98 | 707.3 | 942.9891 |  | 942.634 | 0.12611 | -0.03766% |  |  | 942.634
[9 empty] | 85 | 433.6 | 578.0858 |  | 99 | 733.2 | 977.5196 |  | 976.8724 | 0.41888 | -0.06621% |  |  | 976.8724
[9 empty] | 86 | 450.9 | 601.1506 |  | 100 | 760 | 1013.25 |  | 1012.0752 | 1.3801 | -0.1159% |  |  | 1012.0752
[9 empty] | 87 | 468.7 | 624.8819
[9 empty] | 88 | 487.1 | 649.4133
[9 empty] | 89 | 506.1 | 674.7445
[9 empty] | 90 | 525.8 | 701.009
[9 empty] | 91 | 546 | 727.9401
[9 empty] | 92 | 567 | 755.9378
[9 empty] | 93 | 588.6 | 784.7355
[9 empty] | 94 | 610.9 | 814.4663
[9 empty] | 95 | 633.9 | 845.1305
[9 empty] | 96 | 657.6 | 876.7279
[9 empty] | 97 | 682.1 | 909.3919
[9 empty] | 98 | 707.3 | 942.9891
[9 empty] | 99 | 733.2 | 977.5196
[9 empty] | 100 | 760 | 1013.25
In this block below line 105, I create a spliced "combined" function for e(T), equal to Lowe's up to 62.276 degrees, then my own cubic fit up to 100
|  |  | 60 | 60 |  |  | 199.3881 | Lowe |  |  |  | 199.3881 |  |  | 199.3881 | [9 empty] | 199.3881
|  |  | 60 | 60 |  |  | 199.6304 | me |  |  |  | 199.6304 |  |  | 199.6304 | [9 empty] | 199.6304
[7 empty] | 62.276 | breakover threshold
|  |  | 60 | 60 |  |  | 199.3881 |  |  |  |  | 199.3881 |  |  | 199.3881 | [9 empty] | 199.3881
|  |  | 61 | 61 |  |  | 208.8179 |  |  |  |  | 208.8179 |  |  | 208.8179 | [9 empty] | 208.8179
|  |  | 62 | 62 |  |  | 218.6265 |  |  |  |  | 218.6265 |  |  | 218.6265 | [9 empty] | 218.6265
|  |  | 63 | 63 |  |  | 228.7341 |  |  |  |  | 228.7341 |  |  | 228.7341 | [9 empty] | 228.7341
|  |  | 64 | 64 |  |  | 239.202 |  |  |  |  | 239.202 |  |  | 239.202 | [9 empty] | 239.202

## unsaturated vapor pressure
http://www.wrh.noaa.gov/slc/projects/wxcalc/formulas/rhTdFromWetBulb.pdf
Relative Humidity and Dewpoint Temperature from
Temperature and Wet-Bulb Temperature
quote:
Then, an actual vapor pressure (e) can be calculated using the
equation below:
e = ew − psta × (T − Tw) × 0.00066 × (1 + (0.00115 × Tw))

## Ward Constants
Table 1, Ward 1980
A | Symbol | Parameter | Value
ρ | rho | water density | 0.99983 + 5*10^-5*T - 6.25*10^-6*T^2 | g/cm3 | Here, T = water temperature, in degrees Celsius. Variation of water density with temperature is represented with sufficient accuracy for present purposes by a quadratic dependency.
p | p | atmospheric pressure | 1000 | mbar | Ward uses 1000 mbar, but pressure as a function of altitude has been substituted in the model
ϵr | eta sub r | water emissivity | 0.97 | per day | Ward has this term as dimensionless, but after performing dimensional analysis, it has been determined to need a units of per day
σ | sigma | Stefan-Boltzman constant | 1.171e-07 | cal/(cm2 • K4 • day)
Rν | R sub nu | specific gas constant for water vapor | 0.11 | cal/(g • K)
L | L | latent heat of vaporization | L = a + bTcal/g; a = 595.9 cal/g ; b = -0.545 cal/g/K | cal/g | T = water temperature, in degrees Celsius
cp | c sub p | specific heat | 0.24 | cal/(g • K)
ϵ | eta | molecular weight ratio, water vapor:dry air | 0.622 |  | dimensionless
Test of temperature dependent formulae
T | rho | water density | 0.99602 | g/cm3 | Linear function of temperature in degrees celsius
29 | L | latent heat of vaporization | 580.095 | cal/g | Linear function of temperature in degrees celsius
Plug in environmental values on sheet "Equation 1 2 3 14"
| Ta | air temperature | 28 | Example input value
| Twb | wet bulb air temperature | 26 | Example input value
| T | ambient water temperature | 29 | Example input value
| W | wind in mph at 2m | 20 | Example input value
Derived
| e(T) | saturation vapor pressure over natural water | 40.0708 | mb | from Equation 12
| e(Twb) | saturation vapor pressure calculated on the basis of wet bulb temperature | 33.6224 | mb
| ea | vapor pressure of air | 32.263 | mb | from: http://www.wrh.noaa.gov/slc/projects/wxcalc/formulas/rhTdFromWetBulb.pdf
| e(T) | saturation vapor pressure over heated pond | 42.4468 | mb
T | rho | heated water density | 0.99571 | g/cm3
30 | L | latent heat of vaporization, heated water | 579.55 | 595.9 | -0.545
Calculate
| T' | pond temperature | 30 | Example input value
Conversion constants
| 1 | cal | 4.186 | J
| 1 | mb | 1 | hectopascal | 0.1 kpas

## Ward Eqn 12
Ward 1980 equation 12
595.9 | -0.545 | 0.11 | 29 | Natural water temperature
a | b | Rν | T
Constants arranged on row 2 to make formula 12 more readable |  |  | 30 | Heated water temperature
e(T) = 6.11*exp(((a-273*b)/Rν)((1/273)-(1/(T+273)))+(b/Rν)*ln((T+273)/273))
'=6.11*EXP(((A1-273*B1)/R1)*((1/273)-(1/(T1+273)))+(B1/R1)*LN((T1+273)/273))
40.0708 | millibars at natural water temperature
42.4468 | millibars at heated water temperature
I got the value of 6.1078 from
http://www.faqs.org/faqs/meteorology/temp-dewpoint/
|  |  | T | e(T)
|  |  | 0 | 6.1078
|  |  | 1 | 6.5663
|  |  | 2 | 7.0551
|  |  | 3 | 7.5758
|  |  | 4 | 8.1303
|  |  | 5 | 8.7203
|  |  | 6 | 9.3478
|  |  | 7 | 10.015
|  |  | 8 | 10.7237
|  |  | 9 | 11.4764
|  |  | 10 | 12.2752
|  |  | 11 | 13.1226
|  |  | 12 | 14.0211
|  |  | 13 | 14.9732
|  |  | 14 | 15.9818
|  |  | 15 | 17.0495
|  |  | 16 | 18.1793
|  |  | 17 | 19.3742
|  |  | 18 | 20.6375
|  |  | 19 | 21.9724
|  |  | 20 | 23.3822
|  |  | 21 | 24.8705
|  |  | 22 | 26.441
|  |  | 23 | 28.0975
|  |  | 24 | 29.8438
|  |  | 25 | 31.684
|  |  | 26 | 33.6224
|  |  | 27 | 35.6633
|  |  | 28 | 37.8112
|  |  | 29 | 40.0708
|  |  | 30 | 42.4468
|  |  | 31 | 44.9443
|  |  | 32 | 47.5683
|  |  | 33 | 50.3241
|  |  | 34 | 53.2173
|  |  | 35 | 56.2535
|  |  | 36 | 59.4384
|  |  | 37 | 62.7781
|  |  | 38 | 66.2788
|  |  | 39 | 69.9467
|  |  | 40 | 73.7885
|  |  | 41 | 77.8108
|  |  | 42 | 82.0207
|  |  | 43 | 86.4252
|  |  | 44 | 91.0317
|  |  | 45 | 95.8477
|  |  | 46 | 100.8809
|  |  | 47 | 106.1393
|  |  | 48 | 111.6311
|  |  | 49 | 117.3646
|  |  | 50 | 123.3485